## Slide 1
Energiewirtschaft - Elektrizitätswirtschaft
Lecture – 16.4.2018
Technische Universität Berlin, Fachgebiet Wirtschafts- und Infrastrukturpolitik (WIP)
Prof. Christian von Hirschhausen, Jens Weibezahn, Richard Weinhold
Energy Sector Modeling
Notes: 1

## Slide 2: Agenda - Lecture 5
Physical Grid Constraints - Overview
Physical Flows – General description
Physical Flows – Mathematical description
Modeling – DC Load Flow implementation
Exercise – Revision and Data-handling

## Slide 3: Physical Flow - Introduction
Commercial vs. Physical Flows:
  Assumption: Market is cleared
    What are the resulting line flows?
    Flows according to the laws of physics
    Topology taken into account

## Slide 4: Physical Grid Constraints - Electricity Markets
Single price for all nodes
  Market dispatch for entire network
  Only supply and demand goes into the optimization
  No transmission network included (“copper plate”)
  Congested lines no constraint for the market
  Congestions are dealt in an ex-post analysis redispatch
Uniform
Pricing
Multiple Zones
  Separation of market in several zones with nodes
  Only Exchange constraints between zones
  Zones according to congested lines (if possible)
  Feasible solution if all congestions in between zones, redispatch otherwise
  Example: Nordpool market, Essentially EU
Zonal Pricing
Nodal markets
  Every nodes is its own market
  Full transmission network is part of the market clearing
  Congestions are part of the overall electricity price
  Better market dispatch as higher utilization of available transmission capacity
  Example: PJM market
Locational
Marginal
Pricing

## Slide 5: Physical Flow - Introduction
Commercial vs. Physical Flows:
  Assumption: Market is cleared
    What are the resulting line flows?
    Flows according to the laws of physics
    Topology taken into account
Economic Topics:
  How do we clear the market with line flows in mind?
    Load Flow Constraints
  Adjust the market result to account for line capacities?
    Redispatch
  Take Outages into account
    N-1 Criterion
Technical Topics:
  Ensure secure operation based on the actual grid parameters
  Balance reactive power demand

## Slide 6: General Derivation: Load Flow
Transport versus Load Flow Model:
Flows are inverse proportional to “line resistance”
Source: Eßer et al. (2009).

## Slide 7: Physical Flows – Mathematical description
Fundamental Power Flow Equations:
S = P + jQ Apparent Power = Active Power + Reactive Power
Z = R + jX Impedance = Resistance + Reactance
Y = G + jB Admittance = Conductance + Susceptance
To simplify the non-linear equations we make the following assumptions:
Neglecting reactive power flows
Neglecting active power losses. We assume that R << jX, thus the impedances are given as Z ≈ jX and Y ≈ jB
Voltage angles are small (small angle approximation)
The voltage profile is flat, meaning that the voltage amplitude is equal for all nodes
A: Incidence Matrix (Topology)
Bl: Susceptance of Line l
Bd: lxl Matrix with line susceptance on the diagonal

## Slide 8: Physical Flows – Mathematical description
DC Load Flow Assumptions:
Neglecting reactive power flows
Neglecting active power losses. We assume that R << jX, thus the impedances are given as Z ≈ jX and Y ≈ jB
Voltage angles are small (small angle approximation)
The voltage profile is flat, meaning that the voltage amplitude is equal for all nodes
These assumptions result in the PTDF (Power Transfer Distribution Matrix)
Also known as Node-Line Sensitivity Matrix -> Essentially Pl / Pn
With
A: Incidence Matrix (Topology)
Bl: Susceptance of Line l
Bd: lxl Matrix with line susceptance on the diagonal

## Slide 9: Deriving the PTDF:
Building the PTDF Matrix from:
  Network topology (Incidence Matrix)
  Line Susceptance ( approx. 1/ Line Impedance)
  Problem: The equation for nodal balance is linearly dependent and is therefore singular and has no inverse
    Solution: Define reference (or Slack) Node
    This node is removed from the power flow equations
    and sorted back in with the value zero.
    Therefore the PTDF matrix gives all node to line sensitivities under the restriction that the slack node will balance all other grid injections.
  Define Slack Node
  Define Line Susceptance Vector
  Calculate Line Susceptance Matrix
  Calculate Node Susceptance Matrix
    Remove Row/Column of slack-index
    Invert and sort slack back in with value 0
  PTDF = Calculate Line Susceptance Matrix * “inverse” Node Susceptance Matrix

## Slide 10: DC Load Flow in a Dispatch Model
DCLF Mode:
  Cost Minimization
  Nodal Energy Balance that sets the nodal INJ
  Flow on line = vector product of ptdf row and inj
  Upper and lower limits
  Slack balances all injections

## Slide 11: Objective: Welfare Maximization
Price
Demand; Supply
merit order
cn(g)
Marginal costs of total production
Social welfare
Demand curve
pn(d)
Consumer surplus
Producer surplus
pnopt
dnopt
Notes: Social Welfare = Consumers Willignes to pay – costs of generation

## Slide 12: Ehrenmann, Smeers: The Model
Welfare Maximization:
  Overall Variable Q
    for demand
    And supply
  Underlying Grid
    Constraints for lines 1-6 and 2-5
  Different Constraints
    regarding market zones,
    Market prices
    line capacities

## Slide 13: Overview/outlook:
Load Flow Calculation based on a cleared market
  Active power: commodity
  Reactive Power: Ancillary service
Load Flow in the Market Clearing
  Physical Flows as constraint in the model
Homework 3: Ehremann, Smeers as example of how different implementations yields different